Standard EC.02.05.05

The hospital inspects, tests, and maintains utility systems.

Note: At times, maintenance is performed by an external service. In these cases, hospitals are not required to possess maintenance documentation, but must have access to such documentation during survey and as needed.

Elements of Performance for EC.02.05.05

EC.02.05.05EP1- When performing repairs or maintenance activities, the hospital has a process to manage risks associated with air-quality requirements; infection control; utility requirements; noise, odor, dust, vibration; and other hazards that affect care, treatment, or services for patients, staff, and visitors.

### Recommended Document:

- Policy on the Repair and Maintenance Risk Management

### Examples:

UT-EC.02.05.05 EP1 a Policy on Repair & Maint Risk Management

UT-EC.02.05.05 EP1 b Comprehensive RMRA Tool

UT-EC.02.05.05 EP1 c Air Quality Assessment Tool

UT-EC.02.05.05 EP1 d Noise Vibration Assessment Tool

UT-EC.02.05.05 EP1 e Utility Systems Assessment Tool

UT-EC.02.05.05 EP1 f Other Hazards Assessment Tool

UT-EC.02.05.05 EP1 g Odor Risk Assessment Tool

EC.02.05.05EP2- The hospital tests utility system components on the inventory before initial use and after major repairs or upgrades. The completion date and the results of the tests are documented.

### Recommended Documents:

- Policy on the Preventative Maintenance & Testing of Utility Systems

### Examples:

UT-EC.02.05.05EP2  Initial Testing of Utility Systems

The hospital inspects, tests, and maintains the following (EPs3-5):

EC.02.05.05EP4- The hospital inspects, tests, and maintains the following: High-risk utility system components on the inventory. The completion date and the results of the activities are documented. Note 1: A high-risk utility system includes components for which there is a risk of serious injury or even death to a patient or staff member should it fail, which includes life-support equipment. Note 2: Required activities and associated frequencies for maintaining, inspecting, and testing of utility systems components completed in accordance with manufacturers’ recommendations must have a 100% completion rate.

Note 3: Scheduled maintenance activities for high-risk utility systems components in an alternative equipment maintenance (AEM) program inventory must have a 100% completion rate.

EC.02.05.05EP5- The hospital inspects, tests, and maintains the following: Infection control utility system components on the inventory. The completion date and the results of the activities are documented.

Note 1: Required activities and associated frequencies for maintaining, inspecting, and testing of utility systems components completed in accordance with manufacturers’ recommendations must have a 100% completion rate. Note 2: Scheduled maintenance activities for infection control utility systems components in an alternative equipment maintenance (AEM) program inventory must have a 100% completion rate.

EC.02.05.05EP6- The hospital inspects, tests, and maintains the following: Non-high-risk utility system components on the inventory. The completion date and the results of the activities are documented.

Note: Scheduled maintenance activities for non-high-risk utility systems components in an alternative equipment maintenance (AEM) program inventory may be deferred as defined by organization policy, provided the completion rate is not less than 100%.

### Recommended Document:

### A policy on inspecting, testing and maintaining high-risk, infection control and non-high-risk equipment.

### A form of the high-risk equipment.

### A form of the infection control equipment.

### A form of the non-high-risk equipment.

### Examples:

UT-EC.02.05.05EP4-6 a Policy on Testing Utility Systems

UT-EC.02.05.05EP4 b Testing High-risk Utility Systems

UT-EC.02.05.05EP5 c Testing Infection Control Operational Components

UT-EC.02.05.05EP6 d Testing Non-High-risk Utility Systems

EC.02.05.05EP7-  Line isolation monitors (LIM), if installed, are tested at least monthly by actuating the LIM test switch per NFPA 99-2012: 6.3.2.6.3.6, which activates both visual and audible alarms. For LIM circuits with automated self-testing, a manual test is performed at least annually. LIM circuits are tested per NFPA 99-2012: 6.3.3.3.2 after any repair or renovation to the electric distribution system. Records

are maintained of required tests and associated repairs or modifications, containing date, room or area tested, and results. (For full text, refer to NFPA 99-2012: 6.3.2; 6.3.3; 6.3.4)

### Recommended Document:

- Insert your policy for Line Isolation Monitor Testing

### Examples:

UT-EC.02.05.05EP7 a Policy for Line Isolation Monitor Testing

EC.02.05.05EP8- The hospital meets all other HealthCare Facilities Code requirements for electrical distribution, HVAC. (For full text, refer to NFPA 99-2012: Chapters 6 and 9). Note: For hospitals that use Joint Commission accreditation for deemed status purposes: the hospital meets the applicable provisions of the Life Safety Code Tentative Interim Amendments (TIAs) 12-2 and 12-3.

### Recommended Document:

Information is provided in the EC.01.01.01EP8 Utility Management Plan

### Examples:

UT-EC.02.05.05EP8 a Meeting the Requirements of NFPA 99-2012 Chapters 6 & 9