## Supervisory Signal Devices
<<Facility Name>>
<<City, State>>
Activity Record
Supervisory Signal Devices
EC.02.03.05, EP 1
Tested - Quarterly and in accordance with NFPA 72-2010 Edition (14.4.5)
Conducted by: | <<John Doe, (Hospital Name) Facilities (555) 555-5555>>
Performance Data |  | Pass | Fail | N/A | Comments
Control Valve Supervisory Signal
Signal received indicating movement of the valve from its normal position?
Signal received indicating restoration of the valve to its normal position?
Pressure Supervisory Signal
Signal received indicating required pressure has increased or decreased?
Signal received indicating restoration of the pressure to its normal position?
High-or low-air pressure switches operated?
Signal received where the required pressure is increased or decreased a maximum 10 psi from the required pressure?
High-or low-air pressure switches operated for dry-pipe sprinkler?
Signal received where the required pressure is increased or decreased a maximum 10 psi from the required pressure for a dry-pipe sprinkler?
High-or low-air pressure switches operated for steam pressure?
Signal received where prior to the pressure falling below 110% of the minimum operating pressure required for steam-operated equipment?
Conducted by: | <<John Doe, (Hospital Name) Facilities (555) 555-5555>>
Performance Data |  | Pass | Fail | N/A | Comments
Fire Pump Water Level Supervisory Signal
Signal received indicating required water level has been lowered or raised?
Signal received indicating restoration?
Signal received where the water level raised or lowered 3 inches from the required level?
Signal for other than the pressure tanks shall initiate low-water level signal when the water level falls 12 inches?
Fire Pump Water Temperature Supervisory Signal
Water temperature switches were operated?
Signal received if the water temperature decreased to 40°F?
If the room temperature decreased to 40°F, was the restoration to at least 40°F verified?
Room Temperature Supervisory Signal
Room temperature switch operated?
Signal was received if room temperature decreased to 40°F?
If the room temperature decreased to 40°F, was the restoration to at least 40°F verified?
Sprinkler system, other fire suppression systems
Signal indicating an off-normal condition?
Elevator Shutdown
Control circuits to shut down elevator power was indicated when loss of voltage at control unit and required remote annunciators?