~Fire & Smoke Protection

Standard LS.02.01.30

The hospital provides and maintains building features to protect individuals from the hazards of fire and smoke.

Rationale for LS.02.01.30

Fire and smoke are special concerns in health care organizations because of the inability of some [patient]s to evacuate without assistance from staff. If not properly protected, the building can put [patient]s at risk because smoke and fire can travel through openings in a building. To facilitate safe evacuation, the effects of fire and smoke can be contained when sections of a building are separated into multiple compartments. In addition, interior finishes need to be controlled to minimize smoke and toxic gases. Openings are necessary and include such features as heating, ventilating, and air conditioning (HVAC) systems, elevator shafts, and trash and laundry chutes. hospitals should design and maintain these openings to contain fire to a compartment or floor.

LS.02.01.30EP1-In new construction, vertical openings, including exit stairs, are enclosed by one-hour fire-rated walls when connecting three or fewer floors and two-hour fire-rated walls when connecting four or more floors. Existing vertical openings, including exit stairs, are enclosed with a minimum of one-hour fire-rated construction.

Note: These vertical openings include, but are not limited to, shafts (including elevator, light and ventilation), communicating stairs, ramps, trash chutes, linen chutes, and utility chases. (For full text, refer to NFPA 101-2012: 8.6; 18/19.3.1; 7.1.3.2.1)

LS.02.01.30EP2-All new hazardous areas have doors that are self-closing or automatic-closing, except for laboratories using flammable or combustible materials deemed less than a severe hazard and storage rooms greater than 50 square feet, but less than 100 square feet that are used for storage of combustible material. Hazardous areas have a fire barrier with a one-hour fire-resistive rating. These areas include, but are not limited to, boiler and fuel-fired heater rooms, central/bulk laundries larger than 100 square feet, paint shops, repair shops, soiled linen rooms, trash collection rooms with containers exceeding 64 gallons, laboratories considered a severe hazard, and storage rooms larger than 100 square feet that contain combustible material. (For full text, refer to NFPA 101-2012: 18.3.2.1; 18.3.2.2; 18.3.2.3; 18.3.2.4; Table 18.3.2.1)

Note: For hospitals that use Joint Commission accreditation for deemed status purposes: Doors to rooms containing flammable or combustible materials are provided with positive latching hardware. Roller latches are prohibited on such doors.

LS.02.01.30EP3-All existing hazardous areas have doors that are self-closing or automatic-closing. These areas are protected by either a fire barrier with one-hour fire-resistive rating or an approved electrically supervised automatic sprinkler system. Hazardous areas include, but are not limited to, boiler and fuel-fired heater rooms, central/bulk laundries larger than 100 square feet, paint shops, repair shops, soiled linen rooms, trash collection rooms with containers exceeding 64 gallons, laboratories employing flammable or combustible materials deemed less than a severe hazard, and storage rooms greater than 50 square feet used for storage of equipment and combustible supplies. (For full text, refer to NFPA 101-2012: 19.3.2.1; 19.3.2.2; 19.3.2.3; 19.3.2.4)

Note: For hospitals that use Joint Commission accreditation for deemed status purposes: Doors to rooms containing flammable or combustible materials are provided with positive latching hardware. Roller latches are prohibited on such doors.

LS.02.01.30EP4-Laboratories using quantities of flammable, combustible, or hazardous materials that are considered a severe hazard are in accordance with NFPA 101-2012: 8.7 and NFPA 99 requirements applicable to administration, maintenance, and testing. (For full text refer to NFPA101-2012: 18/19.3.2.2; NFPA 99-2012: 15.4)

LS.02.01.30EP5-Where residential or commercial cooking equipment is used to prepare meals for less than 31 people in a smoke compartment, one cooking facility is permitted to be open to the corridor provided all criteria in NFPA 101-2012: 18/19.3.2.5 are met.

Note: For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital meets the applicable provisions of the Life Safety Code Tentative Interim Amendment (TIA) 12-2.

LS.02.01.30EP6-Alcohol-based hand rubs (ABHR) are stored and handled in accordance with NFPA 101-2012: 8.7.3.1, unless all of the following conditions are met:

- Corridor is at least six feet wide

- ABHR does not exceed 95% alcohol

- Maximum individual dispenser capacity is 0.32 gallon of fluid (0.53 gallon in suites) or 18 ounces of NFPA Level 1–classified aerosols

- Dispensers have a minimum of four feet of horizontal spacing between them

- Dispensers are not installed within one inch of an ignition source

- If floor is carpeted, the building is fully sprinkler protected

- Operation of the dispenser complies with NFPA 101-2012: 18/19.3.2.6(11)

- ABHR is protected against inappropriate access

- Not more than an aggregate of 10 gallons of fluid or 135 ounces of aerosol are used in a single smoke compartment outside a storage cabinet, excluding one individual dispenser per room

- Storing more than five gallons of fluid in a single smoke compartment complies with NFPA 30

LS.02.01.30EP7-Existing wall and ceiling interior finishes are rated Class A or B for limiting smoke development and the spread of flames. Newly installed wall and ceiling interior finishes are rated Class A. (For full text, refer to NFPA 101-2012: 18/19.3.3; 10.2)

LS.02.01.30EP8-Newly installed interior floor finishes in corridors of smoke compartments with an approved automatic sprinkler system is at least Class II. Existing floor finishes are not restricted. (For full text, refer to NFPA 101-2012: 18/19.3.3; 10.2.7)

LS.02.01.30EP9-Corridors must be separated from all other areas by approved partitions, unless the space is permitted to be open in accordance with NFPA 101-2012: 18/19.3.6.1.

LS.02.01.30EP10-In existing buildings, corridor wall partitions are fire resistance rated for 1/2 hour, continuous from the floor slab to the floor or roof slab above, extended through any concealed spaces (such as those above suspended ceilings and interstitial spaces), properly sealed, and constructed to limit the transfer of smoke. (For full text, refer to NFPA 101-2012: 19.3.6.2)

LS.02.01.30EP11-Within corridors in smoke compartments that are protected throughout with an approved supervised sprinkler system, partitions are allowed to terminate at the ceiling if the ceiling is constructed to limit the passage of smoke. The passage of smoke can be limited by an exposed, suspended-grid acoustical tile ceiling with penetrating items such as sprinkler piping and sprinklers that penetrate the ceiling, ducted heating, ventilating, and air-conditioning (HVAC) supply and return-air diffusers, speakers, and recessed lighting fixtures. (For full text, refer to NFPA 101-2012: 18/19.3.6.2)

LS.02.01.30EP12-In new buildings, all corridor doors are constructed to resist the passage of smoke, hinged so that they swing, and the doors do not have ventilating louvers or transfer grills (with the exception of bathrooms, toilets, and sink closets that do not contain flammable or combustible materials). Undercuts are no larger than one inch. Positive latching hardware is required. Roller latches are prohibited. (For full text, refer to NFPA 101-2012: 18.3.6.3.1; 18.3.6.3.5; 18.3.6.4; 18.3.6.5; 18.3.6.3.10; 18.3.6.3.11)

LS.02.01.30EP13- In existing buildings, all corridor doors are constructed to resist the passage of smoke and constructed of 1 3/4-inch or thicker solid bonded wood core or constructed of material that resists fire for not less than 20 minutes, and the doors do not have ventilating louvers or transfer grills (with the exception of bathrooms, toilets, and sink closets that do not contain flammable or combustible materials). Positive latching hardware is required. Roller latches are prohibited. (For full text, refer to NFPA 101-2012: 19.3.6.3.1; 19.3.6.3.2; 19.3.6.3.5)

Note 1: For hospitals that use Joint Commission accreditation for deemed status purposes:

Powered corridor doors are equipped with positive latching hardware unless the organization can verify that this equipment is not an option provided by the door manufacturer. In instances where positive latching hardware is not an available option provided by the manufacturer, the device used must be capable of keeping the door fully closed when a force of 5 lbf is applied at the latch edge and in any direction to a sliding or folding door, whether or not power is applied in accordance with NFPA 101-2012: 19.3.6.3.7.

Note 2: For hospitals that use Joint Commission accreditation for deemed status purposes:

Doors to toilet rooms, bathrooms, shower rooms, sink closets, and similar auxiliary spaces that

do not contain flammable or combustible materials are not required to have a device capable of

keeping the door fully closed if a force of 5 lbf is applied at the latch edge. In these cases, roller latches are permissible.

LS.02.01.30EP14-In smoke compartments without sprinkler systems, fixed fire windows in corridor walls are 25% or less of the size of the corridor walls in which they are installed. Existing window installations that conform to previously accepted Life Safety Code criteria (such as a size of 1,296 square inches or less, made with wired glass or fire-rated glazing, and set in approved metal frames) are permitted. (For full text, refer to NFPA 101-2012: 19.3.6.2.7; 8.3.3.8; 8.3.3.9; 8.3.3.11)

LS.02.01.30EP15-Openings in vision panels or doors in corridor walls (other than in smoke compartments containing patient sleeping rooms) are installed at or below one half the distance from the floor to the ceiling. These openings may not be larger than 80 square inches in new buildings or larger than 20 square inches in existing buildings.

Note: Openings may include, but are not limited to, mail slots and pass-through windows in areas such as laboratories, pharmacies, and cashier stations. (For full text, refer to NFPA 101-2012: 18/19.3.6.5)

LS.02.01.30EP16-Corridors serving adjoining areas are not used for a portion of an air supply, air return, or exhaust air plenum.

Note: Incidental air movement between rooms and corridors (such as isolation rooms) because of the need for pressure differentials in hospitals is permitted. In such cases, the direction of airflow is not the focus for this element of performance. For the purpose of fire protection, air transfer should be limited to the amount necessary to maintain positive or negative pressure differentials. (For full text, refer to NFPA 101-2012: 19.5.2.1; NFPA 90A-2012: 4.3.12.1; 4.3.12.1.3.2)

LS.02.01.30EP17-In new buildings, at least two smoke compartments are provided for every story with patient sleeping or treatment rooms and for those stories that have an occupant capacity of 50 or more people, regardless of use. Smoke barriers have a minimum one-hour fire resistance rating; the maximum size of each smoke compartment is limited to 22,500 square feet. Space shall be provided on each side of smoke barriers to adequately accommodate the total number of occupants in adjoining compartments. The travel distance from any point within the compartment to a smoke barrier door is no more than 200 feet. (For full text, refer to NFPA 101-2012: 18.3.7.1;18.3.7.3; 18.3.7.5)

LS.02.01.30EP18-In existing buildings, at least two smoke compartments are provided for every story that has more than 30 patients in sleeping rooms. Smoke barriers have a minimum ½-hour fire resistance rating; the maximum size of each smoke compartment is limited to 22,500 square feet. Space shall be provided on each side of smoke barriers to adequately accommodate the total number of occupants in adjoining compartments. The travel distance from any point within the smoke compartment to a smoke barrier door is no more than 200 feet. (For full text, refer to NFPA 101-2012: 19.3.7.1; 19.3.7.3; 19.3.7.5)

LS.02.01.30EP19-Smoke barriers extend from the floor slab to the floor or roof slab above, through any concealed spaces (such as those above suspended ceilings and interstitial spaces) and extend continuously from exterior wall to exterior wall. All penetrations are properly sealed. (For full text, refer to NFPA 101-2012: 18/19.3.7.3; 8.2.3; 8.5.2; 8.5.6; 8.7)

Note: Polyurethane expanding foam is not an accepted fire-rated material for this purpose.

LS.02.01.30EP20-Doors in smoke barriers are self-closing or automatic-closing, constructed of 1 3/4-inch or thicker solid bonded wood core or constructed to resist fire for not less than 20 minutes, and fitted to resist the passage of smoke. The gap between meeting edges of door pairs is no wider than 1/8 of an inch. In new buildings, undercuts are no larger than 3/4 of an inch, and doors in a means of egress swing in the opposite direction. (For full text, refer to NFPA 101-2012: 18.3.7.6; 18/19.3.7.8; 8.5.4.1; NFPA 80-2010: 4.8.4.1; 6.3.1.7.1)

LS.02.01.30EP21-In smoke compartments without sprinkler systems, fixed fire windows in smoke barrier doors are 25% or less of the size of the doors in which they are installed. Existing window installations that conform to previously accepted Life Safety Code criteria (such as 1,296 square inches or less, wired glass or fire-rated glazing, and are set in approved metal frames) are permitted. (For full text, refer to NFPA 101-2012: 19.3.7.6; 8.3.3; 8.5.4.5)

LS.02.01.30EP22-In new buildings, the smoke damper is not required in the duct passing through a smoke barrier. In existing buildings, ducts that penetrate smoke barriers are protected by approved smoke dampers that close when a smoke detector is activated. The detector is located either within the duct system or in the area serving the smoke compartment. In existing buildings protected by an approved automatic sprinkler system, the damper is not required in the duct. (For full text, refer to NFPA 101-2012: 18/19.3.7.3; 8.3.5.1; 8.5.5; 8.5.5.7)

LS.02.01.30EP23-Approved smoke dampers protect air transfer openings extending through smoke barriers in ceiling spaces that are used as an unducted common plenum for either supply or return air. (For full text, refer to NFPA 101-2012: 18/19.3.7.3; 8.5.5.2)

LS.02.01.30EP24-Every patient sleeping room has an outside window or outside door except newborn nurseries or rooms intended for less than 24-hour stays (such as obstetrical labor beds, recovery beds, and observation beds in the emergency department).

Note: Windows in atrium walls are considered outside windows.

LS.02.01.30EP25-In new buildings constructed after July 5, 2016, the window sill height in patient sleeping rooms does not exceed 36 inches from the floor, except in special nursing care areas (for example, intensive care units, coronary care units, hemodialysis units, and neonatal intensive care units), where window sill height does not exceed 60 inches above the floor.

LS.02.01.30EP26-The hospital meets all other Life Safety Code fire and smoke protection requirements related to NFPA 101-2012: 18/19.3.

### Recommended Documents:

Policy for determining compliance

Examples:

FS-LS.02.01.30EP1-26 Fire & Smoke Protection