~Fire Alarm Systems

Standard LS.02.01.34

The hospital provides and maintains fire alarm systems

### Recommended Documents:

Policy for determining compliance

LS.02.01.34EP1-A fire alarm system is installed with systems and components to provide effective warning of fire in any part of the building in accordance with NFPA 70-2012, National Electric Code and NFPA 72-2011, National Fire Alarm Code.

LS.02.01.34EP2-The master fire alarm control panel is located in an area with a smoke detector or in an area that is continuously occupied and protected, which is an area enclosed with one-hour fire-rated walls and 3/4-hour fire-rated doors. In areas not continuously occupied and protected, a smoke detector is installed at each fire alarm control unit. In a newly designated occupancy, detection is also installed at notification appliance circuit power extenders and supervising station transmitting equipment. Fire alarm system wiring or other transmission paths are monitored for integrity. (For full text, refer to NFPA 101-2012: 18/19.3.4.1; 9.6)

LS.02.01.34EP3-Initiation of the fire alarm system is by manual means and by any required sprinkler system alarm, detection device, or detection system. Manual alarm boxes are provided in the path of egress near each required exit. Manual alarm boxes in patient sleeping areas are not required at exits if manual alarm boxes are located at all nurse’s stations or other continuously attended staff location, provided alarm boxes are visible, continuously accessible, and 200 feet of travel distance is not exceeded. (For full text, refer to NFPA 101-2012: 18/19.3.4.2.1; 18/19.3.4.2.2; 9.6.2.5)

LS.02.01.34EP4-In new buildings, occupant notification is provided automatically in accordance with NFPA 101-2012: 9.6.3 by audible and visual signals. Positive alarm sequence in accordance with 9.6.3.4 is permitted in buildings protected throughout by a sprinkler system. In critical care areas, visual alarms are sufficient. The fire alarm system transmits the alarm automatically to notify emergency forces in the event of a fire. Annunciation zoning for the fire alarm and sprinklers is provided by audible and visual indicators; zones are not larger than 22,500 square feet per zone. (For full text, refer to NFPA 101-2012: 18.3.4.3–18.3.4.4.3; 9.6.4)

LS.02.01.34EP5-In existing buildings, occupant notification is provided automatically in accordance with NFPA 101-2012: 9.6.3 by audible and visual signals. Positive alarm sequence in accordance with 9.6.3.4 is permitted in buildings protected throughout by a sprinkler system. In critical care areas, visual alarms are sufficient. The fire alarm system transmits the alarm automatically to notify emergency forces in the event of a fire. (For full text, refer to NFPA 101-2012: 19.3.4.3; 9.6.4; 9.7.1.1(1))

LS.02.01.34EP6-Activation of the required fire alarm control functions occurs automatically and is provided with an alternative power supply in accordance with NFPA 72-2010. (For full text, refer to NFPA 101-2012: 18/19.3.4.4; 9.6.1; 9.6.5)

LS.02.01.34EP7-The fire alarm signal automatically transmits using one of the provisions of NFPA 101-2012: 9.6.4 (For full text, refer to NFPA 101-2012: 18/19.3.4.)

LS.02.01.34EP8-Smoke detection systems are provided in spaces open to corridors as required by NFPA 101-2012: Chapter 18/19. (For full text, refer to NFPA 101-2012: 18/19.3.4.5.2: 18/19.3.6.1)

LS.02.01.34EP9-The ceiling membrane is installed and maintained in a manner that permits activation of the smoke detection system.  (For full text, refer to NFPA 101-2012: 18/19.3.4.1)

LS.02.01.34EP10-The hospital meets all other Life Safety Code fire alarm requirements related to NFPA 101-2012: 18/19.3.4.)

Examples:

FA-LS.02.01.34 EP1-10 Fire Alarm Systems