~Fire Extinguishing Systems

Standard LS.02.01.35

The hospital provides and maintains systems for extinguishing fires.

LS.02.01.35EP1-The fire alarm system monitors approved automatic sprinkler system components. (For full text, refer to NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.2.1)

LS.02.01.35EP2-The fire alarm system is connected to water flow alarms. (For full text, refer to NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.2)

LS.02.01.35EP3-Piping supports for approved automatic sprinkler systems are not damaged or loose. (For full text, refer to NFPA 101-2012: 18.3.5.1; 19.3.5.3; NFPA 25-2011: 5.2.3.1; 5.2.3.2)

LS.02.01.35EP4-Piping for approved automatic sprinkler systems is not used to support any other item. (For full text, refer to NFPA 25-2011: 5.2.2.2)

LS.02.01.35EP5-Sprinkler heads are not damaged. They are also free from corrosion, foreign materials, and paint and have necessary escutcheon plates installed. (For full text, refer to NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.5; NFPA 25-2011: 5.2.1.1.1; 5.2.1.1.2; NFPA 13-2010: 6.2.6.2.2; 6.2.7.1)

LS.02.01.35EP6-There are 18 inches or more of open space maintained below the sprinkler deflector to the top of storage.

Note: Perimeter wall and stack shelving may extend up to the ceiling when not located directly below a sprinkler head. (For full text, refer to NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.1.1; NFPA 13-2010: 8.5.5.2; 8.5.5.2.1; 8.5.5.3)

LS.02.01.35EP7-At least six spare sprinkler heads, with associated wrenches, are kept in a cabinet that will not exceed 100°F. (For full text, refer to NFPA 101-2012: 18.3.5.1; 19.3.5.3; 9.7.1.1; NFPA 25-2011: 5.4.1.4; 5.4.1.6; NFPA 13-2010: 6.2.9; 6.2.9.1; 6.2.9.3; 6.2.9.6)

LS.02.01.35EP8-In both new buildings and existing buildings, the clothing closets in patient sleeping rooms are not required to have sprinkler protection if the closet does not exceed six square feet. (For full text, refer to NFPA 101-2012: 18/19.3.5.10)

LS.02.01.35EP9-In new buildings, quick response sprinklers are installed in smoke compartments with patient sleeping rooms. (For full text, refer to NFPA 101-2012: 18.3.5.6)

LS.02.01.35EP10-he travel distance from any point to the nearest portable fire extinguisher is 75 feet or less. Portable fire extinguishers have appropriate signage, are installed either in a cabinet or secured on a hanger made for the extinguisher and are at least four inches off the floor. Those fire extinguishers that are 40 pounds or less are installed so the top is not more than 5 feet above the floor. (For full text, refer to NFPA 101-2012: 18/19.3.5.12; 9.7.4.1; NFPA 10-2010: 6.2.1.1; 6.1.3.3.1; 6.1.3.4; 6.1.3.

LS.02.01.35EP11-Class K–type portable fire extinguishers are located within 30 feet of grease-producing ranges, griddles, broilers, or cooking appliances that use vegetable or animal oils or fats, such as deep fat fryers. A placard is conspicuously placed near the extinguisher stating that the fire protection system should be activated prior to using the fire extinguisher. (For full text, refer to NFPA 101-2012: 18/19.3.2.5.1; NFPA 96-2011: 10.10.2; NFPA 10-2010: 5.5.5; 6.6.2)

LS.02.01.35EP12-Grease-producing cooking devices such as deep fat fryers, ranges, griddles, or broilers have an exhaust hood, an exhaust duct system, and grease removal devices without mesh filters. (For full text, refer to NFPA 101-2012: 18/19.3.2.5.1; NFPA 96-2011: 6.1)

LS.02.01.35EP13-The automatic fire extinguishing system for grease-producing cooking devices does the following: deactivates the fuel source, activates the building fire alarm system, and controls the exhaust fans as designed. (For full text, refer to NFPA 101-2012: 18/19.3.2.5.1; NFPA 96-2011: 10.4; 10.6.1; 10.6.2; 8.2.3)

LS.02.01.35EP14-The hospital meets all other Life Safety Code automatic extinguishing requirements related to NFPA 101-2012: 18/19.3.5.

### Recommended Documents:

Policy for determining compliance

Examples:

FS-LS.02.01.35EP1-14 Fire Extinguishing Systems