~Decorations, Receptacles & Heating Devices

Standard LS.02.01.70

The hospital provides and maintains operating features that conform to fire and smoke prevention requirements

LS.02.01.70EP1-Signs are placed prominently at all major entrances indicating “NO SMOKING” and therefore signs that read “NO SMOKING” or display the international symbol for no smoking are not required in any room, ward, or compartment where flammable liquids, combustible gases, or oxygen is used or stored.

LS.02.01.70EP2-In areas where smoking is permitted, ashtrays are safely designated and made of noncombustible material. Metal containers with self-closing cover devices in which ashtrays can be emptied are readily available to all areas where smoking is permitted. (For full test, refer to NFPA 101-2012: 18/19.7.4)

LS.02.01.70EP3-Draperies, curtains (including cubicle and shower curtains), and loosely hanging fabric comply with NFPA 101-2012: 10.3.1. (For full text refer to NFPA 101-2012: 18/19.7.5.1; 18/19.3.5.11; 10.3.1)

Note: Exceptions include shower/bath curtains in addition to window coverings in patient sleeping rooms and non-patient sleeping rooms located in sprinklered compartments where individual drapery or curtain panels do not exceed 48 square feet or total area does not exceed 20% of the wall.

LS.02.01.70EP4-In buildings without sprinkler protection, upholstered furniture purchased on or after July 5, 2016, meets Class 1 or char length and heat release in accordance with NFPA 101-2012: 10.3.2.1 and 10.3.3. Mattresses purchased on or after July 5, 2016, meet char length and heat release criteria in accordance with NFPA 101-2012: 10.3.2.2 and 10.3.4. (For full text, refer to NFPA 101-2012: 18/19.7.5.2; 18/19.7.5.4)

LS.02.01.70EP5-Decorations (for example, photos, paintings, other art) directly attached to the walls, ceiling and non-fire-rated doors are permitted provided they do not exceed 20% of the wall, ceiling, or door areas in spaces in non-sprinklered smoke compartments; 30% in spaces in sprinklered smoke compartments; 50% inside patient sleeping rooms that do not exceed four people in sprinklered smoke compartments.(For full text and exceptions please refer to NFPA 101 2012: 18/19.7.5.6)

LS.02.01.70EP6-Soiled linen and trash receptacles larger than 32 gallons will be stored in rooms protected as hazardous areas.  (For full text, refer to NFPA 101-2012: 18/19.7.5.7)

Note: Containers that are 96 gallons or less are labeled and listed as meeting the requirements of FM Approval Standard 6921 (or equivalent) and are used solely for recycling clean waste (including patient records awaiting destruction) are permitted in an unprotected area.  Those containers that are greater than 96 gallons are stored in a hazardous storage area.

LS.02.01.70EP7-When installed, new engineered smoke control systems are tested in accordance with NFPA 92-2012, Standard for Smoke Control Systems. Existing engineered smoke control systems are tested in accordance with established engineering principles. (For full text, refer to NFPA 101-2012: 18/19.7.7)

LS.02.01.70EP8-Portable space heaters are prohibited in smoke compartments containing sleeping rooms and patient treatment areas.  Non-sleeping rooms that are occupied by staff and separated from the corridor are permitted to have portable space heaters, but must contain heating elements not exceeding 212°F. (For full text and exceptions please refer to NFPA 101-2012: 18/19.7.8)

Note: For this EP nurse’s stations are considered patient treatment areas.

LS.02.01.70EP9-The hospital meets all other Life Safety Code operating feature requirements related to NFPA 101-2012; 18.7/19.7.

### Recommended Documents:

Policy for determining compliance

Examples:

DH-LS.02.01.70 EP1-9 - Decorations, Receptacles, and Heating Devices