~Fire Alarm Systems

Standard LS.03.01.34

The hospital provides and maintains fire alarm systems

Note 1: This standard applies to sites of care where four or more [patient]s at the same time are provided either anesthesia or outpatient services that renders [patient]s incapable of saving themselves in an emergency in the organization.

Note 2: This standard applies to all hospitals seeking accreditation for Medicare certification purposes, regardless of the number of [patient]s rendered incapable.

Note 3: In leased facilities, the elements of performance of this standard apply only to the space in which the accredited organization is located; all exits from the space to the outside at grade level; and any Life Safety Code building systems that support the space (for example, fire alarm system, automatic sprinkler system).

LS.03.01.34EP1-A fire alarm system is installed with systems and components to provide effective warning of fire in any part of the building in accordance with NFPA 70-2012: National Electric Code, and NFPA-2010, National Fire Alarm Code.

LS.03.01.34EP2-The master fire alarm control panel is located in an area with a smoke detector or is in an area that is a continuously occupied and protected environment, which is an area enclosed with one-hour fire-rated walls and ¾ -hour fire-rated doors. In areas not continuously occupied and protected a smoke detector is installed at each fire alarm control unit. In a new building, detection is also installed at notification application circuit power extenders and supervising station transmitting equipment. Fire alarm system wiring, or other transmission paths are monitored for integrity.  (For full text refer to NFPA 101-2012:  20/21.3.4.1; 9.6)

LS.03.01.34EP3-Installation of the fire alarm system is by manual means and by any required sprinkler system alarm, detection device, or detection system. Manual alarm boxes are provided in the path of egress near each required exit and 200 feet of travel distance is not exceeded. (For full text please refer to NFPA 101-2012: 20/21.3.4.2.1; 20/21.3.4.2.2; 9.6.2.5)

LS.03.01.34EP4-For new buildings, occupant notification is provided automatically in accordance with NFPA 101-2012: 9.6.3 by audible and visual signals. Positive alarm sequence in accordance with 9.6.3.4 is permitted in buildings protected throughout by a sprinkler system. In critical areas, visual alarms are sufficient. The fire alarm system transmits the alarm automatically to notify emergency forces in the event of a fire. Annunciation zoning for the fire alarm and sprinklers is provided by audible and visual indicators; zones are not larger than 22,500 square feet per zone. (For full text, refer to NFPA 101-2012: 20.3.4.3-20.3.4.4; 9.6.4)

LS.03.01.34EP5-For existing buildings, occupant notification is provided automatically in accordance with NFPA 101-2012: 9.6.3 by audible and visual signals. Positive alarm sequence in accordance with 9.6.3.4 is permitted in buildings protected throughout by a sprinkler system. In critical care areas, visual alarms are sufficient. The fire alarm system transmits the alarm automatically to notify emergency forces in the event of a fire. (For full text refer to NFPA 101-2012: 21.3.4.3; 9.6.4; 9.7.1.1 (1))

LS.03.01.34EP6-Activation of the required fire alarm control functions occur automatically and is provided with an alternative power supply in accordance with NFPA 72-2010. (For full text refer to NFPA 101-2012: 20/21.3.4.4; 9.6.1; 9.6.5)

LS.03.01.34EP7-The fire alarm signal automatically transmits to one of the following:

- An auxiliary fire alarm system

- Central station fire alarm system

- A proprietary supervising station fire alarm system

- A remote supervising station fire alarm system

(For full text, refer to NFPA 101-2012: 20/21.3.4.3.2; NFPA 101-2012: 9.6.4)

LS.03.01.34EP8-The remote ancillary panel is in a location approved by the local fire department or its equivalent. (For full text, refer to NFPA 101-2012: 20/21.3.4.3, 9.6.3)

LS.03.01.34EP9-The fire alarm system contains an audible and visual evacuation signal throughout the building and provides occupant notification without delay. (For full text, refer to NFPA 101-2012: 20/21.3.4.3, 9.6.3)

LS.03.01.34EP10-The hospital meets all other Life Safety Code fire alarm requirements related to NFPA 101-2012: 20.3.4/21.3.4.

### Recommended Documents:

Policy for determining compliance

Examples:

FA-LS.03.01.34 EP1-10 - Fire Alarm Systems