~Decorations, Receptacles & Heating Devices

Standard LS.03.01.70

The hospital provides and maintains operating features that conform to fire and smoke prevention requirements

Note 1: This standard applies to sites of care where four or more [patient]s at the same time are provided either anesthesia or outpatient services that renders [patient]s incapable of saving themselves in an emergency in the organization.

Note 2: This standard applies to all hospitals seeking accreditation for Medicare certification purposes, regardless of the number of [patient]s rendered incapable.

Note 3: In leased facilities, the elements of performance of this standard apply only to the space in which the accredited organization is located; all exits from the space to the outside at grade level; and any Life Safety Code building systems that support the space (for example, fire alarm system, automatic sprinkler system).

LS.03.01.70EP1-In areas where smoking is permitted, ashtrays are safely designated and made of noncombustible material. Metal containers with self-closing cover devices in which ashtrays can be emptied are readily available to all areas where smoking is permitted. (For full text, refer to NFPA 101-2012: 20/21.7.4)

LS.03.01.70EP2-Smoking is prohibited in any room, ward, or compartment where flammable liquids, combustible gases, or oxygen is used or stored; these areas have signs that read “NO SMOKING” or display the international symbol for no smoking. In facilities where smoking is prohibited, and signs are prominently placed at all major entrances, secondary signs that prohibit smoking in hazardous areas are not required. (For full text refer to NFPA 101-2012: 18/19.7.4)

Note: The secondary sign exception is not applicable to medical gas storage rooms.

LS.03.01.70EP3-Draperies, curtains (including cubicle and shower curtains), and loosely hanging fabric comply with NFPA 101-2012: 10.3.1. For full text refer to NFPA 101-2012: 18/19.7.5.1; 18/19.3.5.11; 10.3.1)

Note: Exceptions include shower/bath curtains in addition to window coverings in patient sleeping rooms and non-patient sleeping rooms located in sprinklered compartments where individual drapery or curtain panels do not exceed 48 square feet or total area does not exceed 20% of the wall.

LS.03.01.70EP4-In buildings without sprinkler protection, upholstered furniture purchased on or after July 5, 2016, meets Class 1 or char length and heat release in accordance with NFPA 101-2012: 10.3.2.1 and 10.3.3. Mattresses purchased on or after July 5, 2016, meet char length and heat release criteria in accordance with NFPA 101-2012: 10.3.2.2 and 10.3.4. (For full text, refer to NFPA 101-2012: 20/21.7.5.2)

LS.03.01.70EP5-The hospital prohibits all combustible decorations unless they meet the criteria of NFPA 101-2012: 20/21.7.5.4.

LS.03.01.70EP6-Soiled linen and trash receptacles larger than 32 gallons will be stored in rooms protected as hazardous areas.  (For full text, refer to NFPA 101-2012: 20/21.7.5.5)

LS.03.01.70EP7-When installed, new engineered smoke control systems are tested in accordance with NFPA 92-2012, Standard for Smoke Control Systems. Existing engineered smoke control systems are tested in accordance with established engineering principles. (For full text refer to NFPA 101-2012: 20/21.7.7)

LS.03.01.70EP8-Portable space heaters are prohibited in smoke compartments containing sleeping rooms and patient treatment areas.  Non-sleeping rooms that are occupied by staff and separated from the corridor are permitted to have portable space heaters, but must contain heating elements not exceeding 212°F. (For full text refer to NFPA 101-2012: 20/21.7.8)

LS.03.01.70E9-The hospital meets all other Life Safety Code operating feature requirements related to NFPA 101-2012: 20/21.7.

### Recommended Documents:

Policy for determining compliance

Examples:

DH-LS.03.01.70 EP1-9 - Decorations, Receptacles, and Heating Devices