POLICY

It is the policy of <<Facility Name>> to maintain the integrity of the means of egress.

## PURPOSE

Because patients are under medical care and in many cases, cannot move on their own to escape the danger of fire, buildings in which patients are cared for must be designed and maintained so patients can be protected in place or moved to safe places in the building (instead of evacuated to a place outside the building). <<Facility Name>> makes sure that a sufficient number of exits exist and that they are configured to provide protection from fire. Egress doors should not be locked in a way that restricts passage to safety. Means of egress include corridors, stairways, and doors that allow individuals to leave a building or to move between specific spaces in the building(s). They allow individuals to escape from fire and smoke and, therefore, are an integral part of a fire protection strategy.

Note: The Life Safety Code does permit select doors to be locked when there are clinical reasons to restrict the movement of the [patient].

RESPONSIBILITY

The <<Facilities Department>> is responsible for maintaining the architectural integrity of the Means of Egress.

PROCEDURE

The organization ensures maintenance of means of egress through its design, maintenance, and surveillance activities.  These activities included but are not necessarily limited to pre-design review of planned construction, final review and walk-thru post construction, regular maintenance activities related to doors, walls, floors, etc., and routine surveillance activities to ensure code compliance.

Areas considered during these activities include but are not limited to things like locking of doors in egress paths, door swing, wall continuity, corridor obstructions, vision panels in fire doors, exit signs, egress illumination, and numerous other Life Safety Code requirements.

- Doors in a means of egress are not equipped with a latch or lock that requires the use of a tool or key from the egress side, unless a compliant locking configuration is used, such as a delayed-egress locking system as defined in NFPA 101-2012: 7.2.1.6.1 or access-controlled egress door assemblies as defined in NFPA 101-2012: 7.2.1.6.2. Elevator lobby exit access door locking is allowed if compliant with 7.2.1.6.3. (For full text, refer to NFPA 101-2012: 18/19.2.2.2.4; 18/19.2.2.2.5; 18/19.2.2.2.6)

Note: For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital meets the applicable provisions of the Life Safety Code Tentative Interim Amendment (TIA) 12-4.

- Doors to patient sleeping rooms are not locked unless the clinical needs of patients require specialized security or where patients pose a security threat and staff can readily unlock doors at all times. (For full text, refer to NFPA 101-2012: 18/19.2.2.2.2; 18/19.2.2.2.5.1; 18/19.2.2.2.5.2)

- Horizontal sliding doors permitted by NFPA 101-2012: 7.2.1.14 that are not automatic closing are limited to a single leaf and have a latch or other mechanism to prevent the door from rebounding. (For full text, refer to NFPA 101-2012: 18/19.2.2.2.10.1)

- Horizontal sliding doors serving an occupant load fewer than 10 are permitted, as long as they comply with NFPA 101-2012: 18/19.2.2.2.10.2 and meet the following criteria:

- Area served by the door has no hazards.

- Door is operable from either side without special knowledge or effort.

- Force required to operate the door in the direction of travel is less than or equal to 30 pounds-force (lbf) to set the door in motion and less than or equal to 15 lbf to close or open to the required width.

- Assembly is appropriately fire rated and is self- or automatic-closing by smoke detection per 7.2.1.8; assembly is installed per NFPA 80-2010.

- Where required to latch, the door has a latch or other mechanism to prevent the door from rebounding.

- Walls containing horizontal exits are fire rated for two or more hours, extend from the lowest       floor slab to the floor or roof slab above, and extend continuously from exterior wall to exterior  wall. (For full text, refer to NFPA 101-2012: 7.2.4.3.1; 18/19.2.2.5)

- Doors in new buildings that are a part of horizontal exits have approved vision panels, are installed without a center mullion, and swing in the opposite direction of one another. Doors in existing construction are not required to swing with egress travel. (For full text, refer to NFPA 101-2012: 18.2.2.5.6; 18.2.2.5.4; 19.2.2.5.3)

- When horizontal exit walls in new buildings terminate at outside walls at an angle of less than 180 degrees, the outside walls are fire rated for 1 hour for a distance of 10 or more feet. Openings in the walls in the 10-foot span are fire rated for 3/4 of an hour. (For full text, refer to NFPA 101-2012: 7.2.4.3.4)

- Outside exit stairs are separated from the interior of the building by walls with the same fire rating required for enclosed stairs. The wall extends vertically from the ground to a point 10 feet or more above the top landing of the stairs or roofline (whichever is lower) and extends 10 feet or more horizontally. (For full text, refer to NFPA 101-2012: 18/19.2.2.3; 7.2.2.5.2; 7.2.2.6.3)

- Stairs and ramps serving as a required means of egress have handrails and guards on both sides in new buildings and on at least one side in existing buildings. Ramps, exit passageways, fire and slide escapes, alternating tread devices, and areas of refuge are in accordance with NFPA 101-2012: 7.2.5–7.5.12. (For full text, refer to NFPA 101-2012: 18/19.2.2.3; 18/19.2.2.6–18/19.2.2.10; 7.2.2.4; 7.2.5–7.2.12)

- New stairs serving three or more stories and existing stairs serving five or more stories have signs on each floor landing in the stairwell that identify the story, the stairwell, the top and bottom, and the direction to and story of exit discharge. Floor level information is also presented in tactile lettering. The signs are placed five feet above the floor landing in a position that is easily visible when the door is open or closed. (For full text, refer to NFPA 101-2012: 18/19.2.2.3; 7.2.2.5.4)

- The capacity of the means of egress is in accordance with NFPA 101-2012: 7.3. (For full text, refer to NFPA 101-2012: 18/19.2.3.1)

- Exits discharge to the outside at grade level or through an approved exit passageway that is continuous and provides a level walking surface. The exit discharge is a hard-packed, all-weather travel surface that is free from obstructions and terminates at a public way or at an exterior exit discharge. (For full text, refer to NFPA 101-2012: 18/19.2.7; 7.1.7; 7.1.10.1; 7.2.6; 7.7.2)

- An exit enclosure is not used for any purpose that has the potential to interfere with its use as an exit and, if so designated, as an area of refuge. Open space within the exit enclosure is not used for any purpose that has the potential to interfere with egress. (For full text, refer to NFPA 101-2012: 18/19.2.2.3; 7.1.3.2.3; 7.2.2.5.3.1)

- Exits, exit accesses, and exit discharges (means of egress) are clear of obstructions or impediments to the public way, such as clutter (for example, equipment, carts, furniture), construction material, and snow and ice. (For full text, refer to NFPA 101-2012:18/19.2.5.1; 7.1.10.1; 7.5.1.1)

Note 1: Wheeled equipment (such as equipment and carts currently in use, equipment used for patient lift and transport, and medical emergency equipment not in use) that maintains at least five feet of clear and unobstructed corridor width is allowed, provided there is

a fire plan and training program addressing its relocation in a fire or similar emergency. (For full text, refer to NFPA 101-2012:18/19.2.3.4 (4))

Note 2: Where the corridor width is at least eight feet and the smoke compartment is fully protected by an electrically supervised smoke detection system or is in direct supervision of facility staff, furniture that is securely attached is allowed provided it does not reduce the corridor width to less than six feet, is only on one side of the corridor, does not exceed 50 square feet, is in groupings spaced at least 10 feet apart, and does not restrict access to building service and fire protection equipment. (For full text, refer to NFPA101-2012: 18/19.2.3.4 (5))

- When stair doors are held open and the sprinkler or fire alarm system activates the release of one door in a stairway, all doors serving that stairway close. (For full text, refer to NFPA 101-2012: 18/19.2.2.2.7; 18/19.2.2.2.8)

- Each floor of a building has at least two exits that are remote from each other and accessible from every part of the floor. Each smoke compartment has two distinct egress paths to exits that do not require entry into the same adjacent smoke compartment. (For full text, refer to NFPA 101-2012: 18/19.2.4.1–18/19.2.4.4)

- Every corridor provides access to at least two approved exits in accordance with NFPA 101-2012: 7.4 and 7.5 without passing through any intervening rooms or spaces other than corridors or lobbies. (For full text, refer to NFPA 101-2012: 18/19.2.5.4)

- In new buildings, exit corridors are at least eight feet wide, unless otherwise permitted by the Life Safety Code. In new psychiatric buildings, exit corridors are at least six feet wide, unless otherwise permitted by the Life Safety Code. (For full text, refer to NFPA 101-2012: 18.2.3.4; 18.2.3.5)

- In existing buildings, exit corridors are at least 48 inches in clear width where serving as a means of egress from patient sleeping rooms. If modifying existing buildings with exit corridors that exceed eight feet, the exit corridors cannot be reduced to less than eight feet. (For full text, refer to NFPA 101-2012: 4.6.12.2; 19.2.3.4)

- Existing exit access doors and exit doors are of the swinging type and are at least 32 inches in clear width. Exceptions are provided for existing 34-inch doors and for existing 28-inch doors where the fire plan does not require evacuation by bed, gurney, or wheelchair. (For full text, refer to NFPA 101-2012: 19.2.3.6, 19.2.3.7)

- New exit access doors and exit doors are of the swinging type and are at least 41 1/2 inches in clear width. In psychiatric hospital doors are at least 32 inches wide. Doors not subject to patient use, in exit stairway enclosures, or serving newborn nurseries are at least 32 inches in clear width. If using a pair of doors, the doors have a rabbet, bevel, or astragal at the meeting edge, and at least one of the doors provides 32 inches in clear width, while the inactive leaf of the pair is secured with automatic flush bolts. (For full text, refer to NFPA 101-2012: 18.2.3.6; 18.2.3.7)

- Exit access doors and exit doors are free of mirrors, hangings, or draperies that might conceal, obscure, or confuse the direction of exit. (For full text, refer to NFPA 101-2012: 18/19.2.1; 18/19.2.5.1; 7.1.10.2; 7.5.2.2.1)

- Doors to new boiler rooms, new heater rooms, and new mechanical equipment rooms located in a means of egress are not held open by an automatic release device. (For full text, refer to NFPA 101-2012: 18.2.2.2.7)

- The corridor width is not obstructed by wall projections. (For full text, refer to NFPA 101-2012: 18/19.2.3.3)

Note: When corridors are six feet wide or more, it is allowable for certain objects to project into the corridor, such as hand rub dispensers or computer desks that are retractable. The objects must be no more than 36 inches wide and cannot project more than 6 inches into the corridor. These items must be installed at least 48 inches apart and above the handrail height. (For full text, refer to NFPA 101-2012: 18/19.2.3.4)

- In new buildings, no dead-end corridor is longer than 30 feet, and the common path of travel does not exceed 100 feet. (For full text, refer to NFPA 101-2012: 18.2.5.2)

Note: Existing dead-end corridors longer than 30 feet are permitted to be used if it is impractical and unfeasible to alter them. (For full text, refer to NFPA 101-2012: 19.2.5.2)

- Patient sleeping rooms open directly onto an exit access corridor. Patient sleeping rooms with less than eight beds may have one intervening room to reach an exit access corridor provided the intervening room is equipped with an approved automatic smoke detection system. (For full text, refer to NFPA 101-2012: 18/19.2.5.6.1–18/19.2.5.6.4)

- Patient sleeping rooms that are larger than 1,000 square feet have at least two exit access doors remotely located from each other. Rooms not used as patient sleeping rooms that are larger than 2,500 square feet have at least two exit access doors remotely located from each other. (For full text, refer to NFPA 101-2012: 18/19.2.5.5)

- Suites are separated from the remainder of the building by corridor walls or existing barriers and doors that limit the transfer of smoke. (For full text, refer to NFPA 101-2012: 18/19.2.5.7.1.2; 18/19.3.6)

- Suites are subdivided by means of noncombustible or limited-combustible partitions or partitions constructed with fire retardant–treated wood enclosed with noncombustible or limited-combustible materials. These partitions are not required to be fire rated. (For full text, refer to NFPA 101-2012: 18/19.2.5.7.1.4)

- Suites of patient sleeping rooms larger than 1,000 square feet are provided with at least two exit access doors remotely located from each other, with one exiting directly to a corridor. The second exit may go into another suite (provided the two suites are separated with a corridor wall), an exit stair, exit passageway, or exit door to the exterior. (For full text, refer to NFPA 101-2012: 18/19.2.5.7.2.1(B); 18/19.2.5.7.2.2)

- Suites not used as patient sleeping rooms that are larger than 2,500 square feet have at least two exit access doors remotely located from each other, with one directly exiting to a corridor. The second exit may go into another suite (provided the two suites are separated with a corridor wall), an exit stair, exit passageway, or exit door to the exterior. (For full text, refer to NFPA 101-2012:18/19.2.5.7.3.2; 18/19.2.5.7.3.1(B))

- For existing buildings, suites of patient sleeping rooms are limited to 5,000 square feet or less. If the existing building has an approved electrically supervised sprinkler system and total coverage automatic smoke detection system, the suite is permitted to be increased to 7,500 square feet. (For full text, refer to NFPA 101-2012: 9.6.2.9; 19.3.4; 19.3.5.7; 19.3.5.8.) If the suite is provided with direct visual supervision, an approved electrically supervised sprinkler system, and a total coverage (complete) smoke detection system, the suite is permitted to be increased to 10,000 square feet. (For full text, refer to NFPA 101-2012: 9.6.2.9; 19.2.5.7.2.1(D)(1)(a); 19.2.5.7.2.3; 19.3.4; 19.3.5.8)

- For new buildings, patient sleeping suites are allowed to be 7,500 square feet. If the suite has total coverage smoke detection and direct visual supervision, the suite can be up to 10,000 square feet. (For full text, refer to NFPA 101-2012: 18.2.5.7.2.3; 18.2.5.7.2.1(D)(1)(a); 18.3.4)

- Patient care suites not used for sleeping are limited to 10,000 square feet. (For full text, refer to NFPA 101-2012: 18/19.2.5.7.3.3)

- For new buildings, sleeping and non-sleeping patient care suites have a travel distance to an exit access door of 100 feet or less from any point in the suite. The travel distance between any point in the suite and an exit is 200 feet. (For full text, refer to NFPA 101-2012:18.2.5.7.2.4; 18.2.5.7.3.4)

- For existing buildings, sleeping and non-sleeping patient care suites have a travel distance to an exit access door of 100 feet or less from any point in the suite. The travel distance between any point in the suite and an exit is either 150 feet if the building is not protected throughout by an approved electrically supervised sprinkler system or 200 feet if the building is fully protected by an approved electrically supervised sprinkler system. (For full text, refer to NFPA 101-2012: 19.2.5.7.2.4; 19.2.5.7.3.4)

- Travel distances to exits are measured in accordance with NFPA 101-2012: 7.6.

- From any point in the room or suite to the exit is 150 feet or less (200 feet or less if the building is fully sprinklered)

- From any point in a room to the room door is 50 feet or less

(For full text, refer to NFPA 101-2012: 18/19.2.6)

- Means of egress are adequately illuminated at all points, including angles and intersections of corridors and passageways, stairways, stairway landings, exit doors, and exit discharges. (For full text, refer to NFPA 101-2012: 18/19.2.8; 7.8.1.1)

- Illumination in the means of egress, including exit discharges, is arranged so that failure of any single light fixture or bulb will not leave the area in darkness (less than 0.2 foot candles). Emergency lighting of at least 1½-hours duration is provided automatically in accordance with NFPA 101-2012: 7.9. (See also EC.02.05.07, EP 2) (For full text, refer to NFPA 101-2012: 18/19.2.8; 18/19.2.9.1; 7.8.1.4; 7.9.2)

- Exit signs are visible when the path to the exit is not readily apparent. Signs are adequately lit and have letters that are four or more inches high (or six inches high if externally lit). Exit and directional signs displayed with continuous illumination are also served by the emergency lighting system unless the building is one story with less than 30 occupants, and the line of exit travel is obvious. (For full text, refer to NFPA 101-2012: 18/19.2.10; 7.10.1.4; 7.10.1.5.1; 7.10.5; 7.10.6; 7.10.7)

- Signs reading "NO EXIT" are posted on any door, passage, or stairway that is neither an exit nor an access to an exit but may be mistaken for an exit. (For full text, refer to NFPA 101-2012: 18/19.2.10.1; 7.10.8.3)

- The hospital meets all other Life Safety Code means of egress requirements related to NFPA 101-2012: 18/19.2.