# POLICY

<<Facility Name>> will test, inspect, and maintain battery-powered lights required for egress such as exit signs and egress lights.

# PROCEDURE

The <<Engineering Department>> is responsible for identifying all battery-powered lights on the inventory installed to provide exit path illumination or for illumination of critical task areas and EXIT signs.  This includes:

- Exit signs

- Illumination for egress

- Egress lights

- Lights in areas that anesthesia procedures are performed

- Indoor emergency generator locations

Monthly Test – Battery Powered Emergency Lighting Systems EXIT Signs, Task Lighting Tests

At least monthly, a functional test of all emergency lighting systems and EXIT signs required for egress and task lighting shall be tested.

  - The test will be for a minimum of 30-seconds.

  - Press the “Test” button or switch, and observe the light remains at approximately the same level of brightness during the entire 30 seconds.

  - If the light begins to fade, notify <<Engineering Department>> to check the battery system.

  - Document the date and results of the test.

Note: Exit lighting should be checked to assure the exit light is illuminated, at the time of the test.  If there are problems, immediately contact <<Engineering Department>>.

Annual Test – Battery Powered Light Tests

Every 12-months

- A functional test of the battery-powered lights that are required for egress will be conducted for a minimum of 1-1/2 hours (90 minutes).

- The illumination may fall to 60% of the original but must provide at least 0.1 foot-candle at the floor after 90 minutes.

- An equivalent battery test that meets the same parameters may be used if desired.  If an alternate test is used, it must be described in a written procedure.

- The results of all tests and inspections must be documented on the log for each light. The documentation must include the date and the name of the individual performing the activity.

- If there are problems, immediately contact <<Engineering Department>>.

For new construction, renovation, or modernization, battery-powered lighting in locations where deep

sedation and general anesthesia are administered is tested annually for 30 minutes. The test results and completion dates are documented.

Monthly Inspection – Exit Lights

At least monthly the facility will perform a visual inspection of exit signs and document the completion date(s) and results on <<attachment II>>.

ATTACHMENT:

Attachment I- Battery-powered Test Log (UT-EC.02.05.07EP1-2 b)

Attachment II- Exit sign inspection log (UT-EC.02.05.07EP1-2 c)