# POLICY

<<Facility Name>>performs all appropriate tests on Stored Emergency Power Supply System (SEPSS).

# PROCEDURE

The <<Engineering Department>> is responsible for performing the appropriate functional test of the Level 1 Stored Emergency Power Supply Systems (SEPSS) on a monthly basis and performs a test of Level 2 SEPSS on a quarterly basis.

Stored Emergency Power Supply System

SEPSS Systems area intended to automatically supply illumination or power to critical areas and equipment essential for safety to human life.  This includes,

- Safe exiting

- Ventilation where essential to maintain life

- Fire detection and alarm systems

- Public Safety communication systems

- Equipment or system that could cause serious life safety or health hazards to patient, visitor or staff if interrupted.

Testing

Quarterly and annually:

- Every quarter, a functional test of the SEPSS is performed for 5 minutes or as specified for its class* (whichever is less)

*Class defines the minimum time for which the SEPSS is designated to operate at it rated load without recharging (See NFPA 111, Standard on Stored Electrical Energy Emergency and Standby Power Systems, 2010 edition.

- Annually, a full load test for 60% of the full duration of its class

- The completion date and the results of the tests are documented and maintained in the <<Engineering Department>>.

Critical Non-SEPSS Systems

Critical Non-SEPSS Systems are battery back-up emergency power system that are considered at non-SEPSS, but have been determined to be critical for operation during an electrical failure by the hospital including, but not limited to:

- Laboratory equipment

- Electronic medical equipment

Testing

Testing should be properly tested and maintained in accordance to manufacturer’s recommendations.  The test date and data are documented maintained in the <<Engineering Department>>.