## Monthly Generator Test Log
<<Facility Name>>
<<City, State>>
Monthly Generator Test Log
(This form can be used to estimate the output in Amps when the nameplate rating is in Kilowatts)
Generator: <<Identifying name>> |  |  |  |  | Run Date:
Operating Time: | Start Time: |  |  | Stop Time: |  |  | Total Time: (min)
Enter data into red cell to calculate output in Amps and 30% operational level*
Normal Operating Voltage | 208 | Volts |  | Transfer Time |  | ATS # | Time
Generator Output in KW (Nameplate rating) | 200 | Kilowatts |  | < = 10 Sec
Conversion into Watts | 200000 | Watts
Power Factor (PF) ( usually considered .8) | 0.8 | PF |  |  | ATS# | Tested
Output in Amps† | 694.7532 | Amps |  |  |  | Pass | Fail
Assuming 100% efficiency |  |  |  |  | #1
#2
#3
30 % of nameplate rating in Amps calculate to be: | 208.426 | Amps |  |  | #4
#5
<<insert other ATSs if needed>>
Generator Test Data | Operating Temp - | Oil Pressure | Operating Voltage | Gauge # 1 Reading | Gauge # 2 Reading | Gauge # 3 Reading | All Gauge Readings ≥ 30% rating |  | Cycles
| (170-230 °F) | (30-60 PSI) | (Volts) | (Amps) | (Amps) | (Amps) | Y | N | (HZ)
Beginning of test at operating temperature
At the 10 minute interval
At the 30 minute interval
Final Readings (test for at least 30 minutes at operating temperature)
Activities | Yes | No | N/A | Notes
Clean area around the generator
Check all fluid levels for proper levels
Check the water coolant protection range: -20°F
Check belts, gaskets and hoses condition/leaks
Check batteries and service batteries
Check charging rate
Check fuel supply in main and day tanks
<<Include other procedures as needed>>
Report any unusual conditions ASAP
Technician Signature |  |  |  | Date
SAFETY FIRST - wear appropriate eye and hearing protection during test
† Amps = KW / (Voltage x PF x 1.73)