# POLICY

<<Facility Name>> performs a four-hour test of the diesel-powered emergency generator at least once every thirty-six (36) months.

# PROCEDURE

- The diesel-powered emergency generator providing emergency power to the life safety and critical power elements will be tested:

- For a duration of four continuous hours

- At least every 36 months

- The emergency generator is tested with either:

- a dynamic or static load of at least 30% of nameplate rating of the generator

OR

- meets the manufacturer’s recommendations for exhaust gas temperature during the test

Note: For non-diesel-powered generators tests need only to be conducted with available load

- If the emergency generator fails a required test, interim measures are implemented to protect patient, visitors, and staff until necessary repairs or corrective action is completed.

- If the emergency generator fails a required test, a complete retest will be conducted after necessary repairs or corrective action is completed

- The completion date and the results of the tests are documented. And will be maintained by the <<Engineering Department>>.