# POLICY

It is the policy of <<Facility Name>> that all piped medical gas system shall be accessible and properly labeled in compliance with the NFPA 99-2012, Chapter 5.

PROCEDURE

- All main supply valves and area control (shut-off) valves for piped medical gas and vacuum systems shall be accessible and clearly labeled.

- Piping is labeled by stencil or adhesive markers identifying the gas or vacuum system, including the name of system or chemical symbol, color code (see NFPA 99-2012: Table 5.1.11), and operating pressure if other than standard.

- Labels are at intervals of 20 feet or less and are in every room, at both sides of wall penetrations, and on every story traversed by riser.

- Piping is not painted.

- All medical gas systems shall be labeled per NFPA 99-2012, Chapter 5. Zone valve labeling shall include the exact rooms or areas that are served by the load side of the zone valve(s). Example: PACU Rooms 1, 2, 3, 5, 6.

- Staff is trained about the locations of the applicable medical gas zone valves, which might be needed during emergencies.

- Shutoff valves are identified with the name or chemical symbol of the gas or vacuum system, room or area served, and caution not to use valve except in an emergency.

- Staff must know who is authorized to shut off during an emergency. The <<administrator, nursing supervisor or his/her designee>> will assess the need if oxygen supply to the affected area should be discontinued.  Only the <<administrator or his/her designee and/or Fire Marshall>> are authorized to order a supply valve closed.  A member of the <<Respiratory Care Department>> will be responsible for closing the valve after ensuring all persons dependent on oxygen delivery systems are properly treated. NOTE: With the exception in Surgery areas only, the Anesthesia personnel will turn off the oxygen. This information is located in the Fire Response Plan

- The accessibility of all shut-off valves, as well as the main control valves, shall undergo regular monitoring during environmental tours to ensure no obstructions exist and a minimum 36-inch clearance is adhered to.