~Building & Fire Protection Features

Standard LS.05.01.10

Building and fire protection features are designed and maintained to minimize the effects of fire, smoke, and heat.

Rationale LS.05.01.10

Not applicable

LS.05.01.10EP1 – When building rehabilitation occurs, the hospital incorporates NFPA 101-2012: Chapters 38,39, and 43, (For full text refer to NFPA 101-2012:  38/39.1.1.3:4.6.7)

LS.05.01.10EP2 - Business occupancies are separated from parking structures by a 2-hour or greater fire barrier, (For full text, refer to NFPA 101-2012: 38/39.1.3.2.1)

LS.05.01.10EP3 – The fire protection rating for opening protectives in fire barriers, fire-rated smoke barriers, and fire-rated smoke partitions is as follows:

- Three hours in 3-hour barriers

- Ninety minutes in 2-hour barriers and partitions

- Twenty minutes in ½ hour barriers and partitions

Labels on fire door assemblies must be maintained in legible condition.  (For full text, refer to NFPA 101-2012: 8.3.4,2; Table8.3.4.2; 8.3.3.2.3; NFPA 80-2010: 5.2.13.3

LS.05.01.10EP4 – Vertical openings must be protected in the following manner:

- Enclosures serving four or more floors in new construction must have a 2-hour fire rating.

- Enclosures serving three or less floors in new construction must ha a 1-hour fire rating.

- Enclosures in existing construction must have a ½ -hour fire rating

- A vertical opening below the street level that contains storage or communicates with a different occupancy must be protected.

(For full text, refer to NFPA 101-2012: 38/39.3)

LS.02.01.10EP5The space around pipes, conduits, bus ducts cables, wire, airducts, or pneumatic tubes penetrating walls or floors are protected with an approved fire-rated material.

Note: Non-approved fire-rated polyurethane expanding foam is not accepted fire-rated material for this purpose. (For full text, refer to NFPA 101-10-12)

LS.02.01.10EP6- Doors requiring a fire rating of ¾ of an hour or longer are free of coverings, decorations, or other objects applied to the door face, with the exception of informational signs, which are applied with adhesive only.  (For full text, refer to NFPA 80-2010; 4.1.4)

LS.02.01.10EP7- The hospital meets all other Life Safety Code requirements related to NFPA 101-2012: 38/39.1.

### Recommended Documents:

Policy for Building and Fire Protection Features

Examples:

BF-LS.05.01.10EP1-7 - Building and Fire Protection Features