~ Hazardous Areas and Protection

Standard LS.05.01.30

The hospital provides and maintains building features to protect individuals from the hazards of fire and smoke.

Rationale for LS.05.01.30

Not applicable

LS.05.01.30EP1-   Hazardous areas are protected from other areas by a 1-hour fire resistance-rated barrier (45-minute opening protectives) or a smoke resistive barrier and automatic sprinklers, Doors must be self-closing or automatic closing with latching hardware.  (For full text, refer to NFPA 101-2012: 38/38.3.2

LS.05.01.30EP2   Interior wall and ceiling finishes must be Class A or B for exits and exit access corridors.  All other areas should be Class A, B, or C.  (For full text, refer to NFPA 101-2012: 38/39.3.3)

LS.05.01.30EP3-   Alcohol-based hand rubs (ABHR) are stored and handled in accordance with NFPA 101-2012: 8.7.3.1 as follows:

- Corridor clear width of 44 inches is not compromised by dispenser.

- ABHR does not exceed 95% alcohol.

- Maximum individual dispenser capacity is 0.32 gallons fluid (0.53 gallons in suites or rooms separated from corridors) or 18 ounces of NFFPA Level 1-classified aerosols.

- Dispensers are not installed within 1 inch of an ignition source.

- If floor is carpeted, the building is fully sprinkler protected.

- Operation of the dispensers must comply with the manufactures’ instructions for use.

- ABHR is protected against inappropriate access.

- Not more than an aggregate of 10 gallons of fluid or 1135 ounces of aerosol are used in a single smoke compartment outside of a storage cabinet, excluding one individual dispenser per room.

- Storing more than 5 gallons of fluid in a single smoke compartment complies with NFPA 30.

LS.05.01.30EP4-   The hospital meets all other Life Safety Code fire and smoke protection requirements related to NFPA 101-2012: 38/39.3.

### Recommended Documents:

Policy for Hazardous Areas and Protection

Examples:

FS-LS.05.01.30EP1-4 Hazardous Areas and Protection