# POLICY

It is the policy of <<Facility Name>> to ensure building and fire protection features are designed and maintained to minimize the effects of fire, smoke, and heat.

# PURPOSE

A building must be designed, constructed, and maintained in order to minimize danger from the effects of fire, including, smoke, heat, and toxic gases.  The structural characteristics of the building, as well as its age, determine the types of fire protection features that are needed.  The features covered in this standard include the structure, automatic sprinkler systems, building separations, and doors.

# PROCEDURE

Prior to entering into any construction, renovation, modernization, or alteration of the building, the organization will ensure there will be no adverse effect on the structure and features of fire protection including but not limited to structural fire proofing, exits, vertical separations, smoke compartmentations, fire walls and doors, shafts, fire/smoke dampers, fire suppression systems etc.

The organization will adhere to all applicable city, state, national and accreditation guidelines regarding the design, installation, and maintenance of features of fire protection for its buildings.  Specifically, the organization will ensure compliance with NFPA 101, Life Safety Code 2012 edition and The Joint Commission standards LS.05.01.10 EP 1 - 7.

- When building rehabilitation occurs, the hospital incorporates NFPA 101-2012; Chapters 38,39, and 43. (For full text, refer to NFPA 101-2012: 38/39.1.1.3; 4.6.7)

- Business occupancies are separated from parking structures by a 2 hour or greater fire barrier.  (For full text, refer to NFPA 101-2012: 38/39.1.3.2.10

- The fire protection ratings for opening protectives in fire barriers are as follows:

-Three hours in 3-hour barriers

-Ninety minutes in 2-hour barriers

-Forty-five minutes in 1-hour barriers

-Twenty minutes in thirty-minute barriers

Labels on fire door assemblies must be maintained in legible condition.

- The space around pipes, conduits, bus ducts, cables, wire, air ducts, or pneumatic tubes penetrating fire-rated walls or floors are protected with an approved fire-rated material.

Note: Non-approved polyurethane expanding foam is not an accepted fire-rated material for this purpose.

- Doors requiring a fire rating of ¾ hour or longer are free of coverings, decorations, or other objects applied to the door face with the exception of informational signs, which are applied with adhesive only.

- <<Facility Name>> meets all other Life Safety Code requirements related to NFPA 101-2012: 38/39.