Standard EC.02.05.07

The hospital inspects, tests, and maintains emergency power systems.

Note: This standard does not require hospitals to have the types of emergency power equipment discussed below. However, if these types of equipment exist within the building, then the following maintenance, testing, and inspection requirements apply.

Rationale for EC.02.05.07

Emergency electrical power supply systems may fail during a power disruption, leaving the hospital unable to deliver safe care, treatment, and services to [patients]s. Testing these systems for sufficient lengths of time at regular frequencies increases the likelihood of detecting reliability problems and reduces the risk of losing this critical resource when it is most needed.

Elements of Performance for EC.02.05.07

EC. 02.05.07EP1 At least monthly, the hospital performs a functional test of emergency lighting systems and exit signs required for egress and task lighting for a minimum duration of 30 seconds, along with a visual inspection of other exit signs. The test results and completion dates are documented. (For full text, refer to NFPA 101-2012: 7.9.3; 7.10.9; NFPA 99-2012: 6.3.2.2.11.5)

EC.02.05.07EP2- Every 12 months, the hospital either performs a functional test of battery-powered lights on the inventory required for egress and EXIT signs for a duration of 1 1/2 hours. For new construction, renovation, or modernization, battery-powered lighting in locations where deep sedation and general anesthesia are administered is tested annually for 30 minutes. The test results and completion dates are documented. (See also LS.02.01.20, EP 39) (For full text, refer to NFPA 101-2012: 7.9.3; 7.10.9; NFPA 99-2012: 6.3.2.2.11.5)

### Recommended Documents:

- Matrix to document testing of battery-powered lights

### Examples:

UT-EC.02.05.07EP1-2 a Policy on Battery Powered Lights

UT-EC.02.05.07EP1-2 b Attachment I- Battery-powered Lights Log

UT-EC.02.05.07EP1-2 c Attachment II- Exit sign inspection Log

EC.02.05.07EP3- The hospital performs a functional test of Level 1 stored emergency power supply systems (SEPSS) every month and performs a test of Level 2 SEPSS every quarter. Test duration is for five minutes or as specified for its class (whichever is less). The hospital performs an annual test at full load for 60% of the full duration of its class. The test results and completion dates are documented.

Note 1: Non–SEPSS battery backup emergency power systems that the hospital has determined to be critical for operations during a power failure (for example, laboratory equipment or electronic medical records) should be properly tested and maintained in accordance with manufacturers' recommendations.

Note 2: Level 1 SEPSS are intended to automatically supply illumination or power to critical areas and equipment essential for the safety of human life. Included are systems that supply emergency power for such functions as illumination for safe exiting, ventilation where it is essential to maintain life, fire detection and alarm systems, public safety communications systems, and processes where the current interruption would produce serious life safety or health hazards to patients, the public, or staff.

Note 3: Class defines the minimum time for which the SEPSS is designed to operate at its rated load without being recharged.

Note 4: For additional guidance, see NFPA 111-2010: 8.4.

### Recommended Document:

### A policy on the testing of the SEPSS system.

### Examples:

UT-EC.02.05.07EP3 a Policy on SEPSS System

EC.02.05.07EP4- At least weekly, the hospital inspects the emergency power supply system (EPSS), including all associated components and batteries. The results and completion dates of weekly inspections are documented. Note: For additional guidance, see NFPA 110-2010: 8.3.1; 8.3.3; 8.3.4; 8.4.1.

EC.02.05.07EP5- At least monthly, the hospital tests each emergency generator beginning with a cold start under load for at least 30 continuous minutes. The cool-down period is not part of the 30 continuous minutes. The results and completion date of the tests are documented.

EC.02.05.07EP6- The monthly tests for diesel-powered emergency generators are conducted with a dynamic load that is at least 30% of the nameplate rating of the generator or meets the manufacturer’s recommended prime movers’ exhaust gas temperature. If the hospital does not meet either the 30% of nameplate rating or the recommended exhaust gas temperature during any test in EC.02.05.07, EP 5, then it must test the emergency generator once every 12 months using supplemental (dynamic or static) loads of 50% of nameplate rating for 30 minutes, followed by 75% of nameplate rating for 60 minutes, for a total of 1 1/2 continuous hours. Note: Tests for non-diesel-powered generators need only be conducted with the available load.

### Recommended Document:

### A policy on emergency generator testing.

2.	A form of the generators and their testing.

### Examples:

UT-EC.02.05.07EP4-6 an Emergency Power Generators and Testing

UT-EC.02.05.07EP4-6 b Form-Attachment I- Emergency Generator Test Log

UT-EC.02.05.07EP4-6 c Form-Attachment II- Individual Generator Test Form

UT-EC.02.05.07EP4-6 d Form-Attachment III-Individual Weekly Generator Maintenance Log

EC.02.05.07EP7- At least monthly, the hospital tests all automatic and manual transfer switches. The test results and completion date of the tests are documented.

### Recommended Document:

### A policy on the Automatic Transfer Switches

### A form of ATS testing.

### Examples:

UT-EC.02.05.07EP7 a Policy on Automatic and Manual Transfer Switch Testing

UT-EC.02.05.07EP7 b Form-Attachment I- Automatic and Manual Transfer Switch Log

EC.02.05.07EP8- At least annually, the hospital tests the fuel quality to ASTM standards. The test results and completion dates are documented. Note: For additional guidance, see NFPA 110-2010: 8.3.8.

### Recommended Documents:

- A policy on testing fuel

- Results from fuel testing including any necessary follow-up

### Examples:

UT-EC.02.05.07EP8 Testing Diesel Fuel

EC.02.05.07EP9- At least once every 36 months, hospitals with a generator providing emergency power for the services listed in EC.02.05.03, EPs 5 and 6, test each emergency generator for a minimum of 4 continuous hours. The test results and completion dates are documented. Note: For additional guidance, see NFPA 110-2010, Chapter 8.

EC.02.05.07EP10- The 36-month diesel-powered emergency generator test uses a dynamic or static load that is at least 30% of the nameplate rating of the generator or meets the manufacturer’s recommended prime movers' exhaust gas temperature. Note: Tests for non-diesel-powered generators need only be conducted with the available load.

### Recommended Document:

1.	A policy on generator testing.

### Examples:

UT-EC.02.05.07EP9-10 a Policy on Four-Hour Generator Testing