~Building & fire Protection Features

Standard LS.03.01.10

Building and fire protection features are designed and maintained to minimize the effects of fire, smoke, and heat.

Note 1: This standard applies to sites of care where four or more [patient]s at the same time are provided either anesthesia or outpatient services that render [patient]s incapable of saving themselves in an emergency in the organization.

Note 2: This standard applies to all hospitals seeking accreditation for Medicare certification purposes, regardless of the number of [patients]s rendered incapable.

Note 3: In leased facilities, the elements of performance of this standard apply only to the space in which the accredited organization is located; all exits from the space to the outside at grade level; and any Life Safety Code building systems that support the space (for example, fire alarm system, automatic sprinkler system).

LS.03.01.10EP1-Buildings meet requirements for construction type and height. In Types I and II construction, alternative protection measures are permitted to be substituted for sprinkler protection in specific areas where state or local regulations prohibit sprinklers. All new buildings contain approved automatic sprinkler systems. Existing buildings contain approved automatic sprinkler systems as required by the construction type. (For full text, refer to NFPA 101-2012: 20/21.1.6.1–20/21.1.6.6; 20/21.3.5)

LS.03.01.10EP2-Interior nonbearing walls in Types I or II construction are constructed of noncombustible or limited-combustible materials. Interior nonbearing walls that are required to have a minimum of two-hour fire resistance rating are made with fire retardant–treated wood and enclosed within noncombustible or limited-combustible materials, provided they are not used as shaft enclosures. (For full text, refer to NFPA 101-2012: 20.1.6.3; 20.1.6.4; 21.1.6.3; 21.1.6.4)

LS.03.01.10EP3-When building rehabilitation occurs, the hospital incorporates NFPA 101-2012: Chapters 20, 21, and 43. (For full text, refer to NFPA 101-2012: Chapter 43; 20/21.1.1.4; 4.6.7)

LS.03.01.10EP4-Ambulatory occupancies located in multioccupancy buildings are separated from health care occupancies by two-hour fire-rated walls and from business occupancies by one-hour fire-rated walls. (For full text, refer to NFPA 101-2012: 20/21.1.3; 20/21.1.4; 20/21.3.7.1)

Note: Per Centers for Medicare & Medicaid Services’ regulation, outpatient surgical departments are classified as ambulatory health care occupancies, regardless of the number of patients served. (For full text, refer to NFPA 101-2012: 20/21.1.3.2; 20/21.3.7.1)

LS.03.01.10EP5-Fire barriers are continuous from outside wall to an outside wall or from one fire barrier to another, or a combination thereof, including continuity through all concealed spaces, such as those found above a ceiling, including interstitial spaces. For those fire barriers terminating at the bottom side of an interstitial space, the construction assembly forming the bottom of the interstitial space must have a fire-resistance rating not less than that of the fire barrier. (For full text, refer to NFPA 101-2012: 8.3.1.2)

LS.03.01.10EP6-The fire protection ratings for opening protectives in fire barriers and fire-rated smoke barriers are as follows:

- Three hours in three-hour barriers

- Ninety minutes in two-hour barriers and

- Forty-five minutes in one-hour barriers and

Note: Doors that separate the ambulatory healthcare occupancy from other tenants or other occupancies (except healthcare occupancies) do not need to meet the 45-minute rating as long as they are constructed of not less than 1 ¾ inch thick, solid bonded wood-core or equivalent and must be equipped with positive latches.

- Twenty minutes in thirty-minute barriers

(For full text, refer to NFPA 101-2012: 8.3.3.2: 8.3.4.2: Table 8.3.4.2; 20/21.3.7.1: NFPA 80-2010:5.2.13.3

Note: 1: Labels on fire door assemblies must be maintained in legible condition.

Note: 2: For hospitals that use Joint Commission accreditation for deemed status purposes:  The hospital meets the applicable provisions of the Life Safety Code Tentative Interim Amendment (TIA) 12-1.

Labels on fire door assemblies must be maintained in legible condition. (For full text, refer to NFPA 101-2012: 8.3.4.2; Table 8.3.4.2; 8.3.3.2.3; NFPA 80-2010: 5.2.13.3)

Note: For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital meets the applicable provisions of the Life Safety Code Tentative Interim Amendment (TIA) 12-1.

LS.03.01.10EP7-Doors within walls and floors that are required to be fire rated have functioning hardware, including positive latching devices and self-closing or automatic-closing devices. Gaps between meeting edges of door pairs are no more than 1/8-inch wide, and undercuts are no larger than 3/4 of an inch. Blocking or wedging open fire-rated doors is prohibited. Doors required to be fire rated in the walls do not have unapproved protective plates greater than 16 inches from the bottom of the door. (For full text, refer to NFPA 101-2012: 8.3.3.1; NFPA 80-2010: 4.8.4.1; 5.2.13.3; 6.3.1.7; 6.4.5)

LS.03.01.10EP8-Doors requiring a minimum fire rating of 3/4 of an hour are free of coverings, decorations, or other objects applied to the door face. Informational signs, which are applied with adhesive only, are allowed provided that the informational signage does not exceed 5% of the door face area. (For full text, refer to NFPA 80-2010: 4.1.4)

LS.03.01.10EP9-Ducts penetrating the walls and floors with a fire-resistance rating of fewer than three hours are protected by dampers that are fire rated for 1 1/2 hours; penetrations of three hours or greater are protected by fire dampers that are fire rated for three hours. (For full text, refer to NFPA 101-2012: 8.3.5.7; 9.2.1; NFPA 90A-2012: 5.4)

LS.03.01.10EP10-The space around pipes, conduits, bus ducts, cables, wires, air ducts, or pneumatic tubes penetrating the walls or floors are protected with an approved fire-rated material.

Note: Non-approved polyurethane expanding foam is not an accepted fire-rated material for this purpose. (For full text, refer to NFPA 101-2012: 8.3.5)

LS.03.01.10EP11-The hospital meets all other Life Safety Code requirements related to NFPA 101-2012: 20/21.1.

### Recommended Documents:

Policy for determining compliance

Examples:

BF-LS.03.01.10EP1-11 -  Building and Fire Protection Features