~Fire Extinguishing Systems

Standard LS.03.01.35

The hospital provides and maintains systems for extinguishing fires.

Note 1: This standard applies to sites of care where four or more [patient]s at the same time are provided either anesthesia or outpatient services that render [patient]s incapable of saving themselves in an emergency in the organization.

Note 2: This standard applies to all hospitals seeking accreditation for Medicare certification purposes, regardless of the number of [patients]s rendered incapable.

Note 3: In leased facilities, the elements of performance of this standard apply only to the space in which the accredited organization is located; all exits from the space to the outside at grade level; and any Life Safety Code building systems that support the space (for example, fire alarm system, automatic sprinkler system).

LS.03.01.35EP1-For new construction, the fire alarm system monitors the components of any required approved automatic sprinkler system. (For full text, refer to NFPA 101-2012: 20/21.3.5.2; 9.7.1.1)

LS.03.01.35EP2-The fire alarm system is connected to the water flow alarms of any required automatic sprinkler system. (For full text, refer to NFPA 101-2012: 20/21.3.4.4; 20/21.3.5; 9.7.1.1)

LS.03.01.35EP3-Piping supports for approved automatic sprinkler systems are not damaged or loose. (For full text, refer to NFPA 101-2012:20/21.3.4.4; NFPA 25-2011: 5.2.1; 5.2.2; 5.2.3)

LS.03.01.35EP4-Approved automatic sprinkler systems piping is not used to support any other item. (For full text, refer to NFPA 101-2012: 20/21.3.4.4; NFPA 25-2011: 5.2.2; NFPA 13-2010: 8.5.5.2; 8.5.5.3)

LS.03.01.35EP5-Sprinkler heads are not damaged and are free from corrosion, foreign materials, and paint. (For full text, refer to NFPA 101-2012: 20/21.3.4.4; NFPA 25-2011: 5.2.1; 5.2.2; NFPA 13-2010: 6.2.6.2; 6.2.7.1)

LS.03.01.35EP6-There is 18 inches or more of open space maintained below a sprinkler deflector to the top of storage. Note: Perimeter wall shelving may extend up to the ceiling when not located directly below a sprinkler head. (For full text, refer to NFPA 101-2012: 20/21.3.4.4; NFPA 25-2011: 5.2.1; 5.2.2; NFPA 13-2010: 8.5.5; 8.5.6)

LS.03.01.35EP7-The travel distance from any point to the nearest portable fire extinguisher is 75 feet or less. Portable fire extinguishers have appropriate signage, are installed in a cabinet or secured on a hanger made for the extinguisher, and are at least four inches off the floor. Those fire extinguishers that are 40 pounds or less are installed so the top is not more than 5 feet above the floor. (For full text, refer to NFPA 101-2012: 20/21.3.5.3; 9.7.4.1; NFPA 10-2010: 6.1.3; 6.2.1)

LS.03.01.35EP8-The hospital meets all other Life Safety Code extinguishing requirements related to NFPA 101-2012: 20/21.3.5.

### Recommended Documents:

Policy for determining compliance

Examples:

FE-LS.03.01.35 EP1-8 - Fire Extinguishing Systems