~Building & Fire Protection Features

Standard LS.05.01.10

Building and fire protection features are designed and maintained to minimize the effects of fire, smoke, and heat.

LS.05.01.10EP1 – When building rehabilitation occurs, the hospital incorporates NFPA 101-2012: Chapters 38,39, and 43, (For full text refer to NFPA 101-2012:  38/39.1.1.3:4.6.7)

LS.05.01.10EP2 - Business occupancies are separated from parking structures by a 2-hour or greater fire barrier, (For full text, refer to NFPA 101-2012: 38/39.1.3.2.1)

LS.05.01.10EP3 – The fire protection ratings for opening protectives in fire barriers are as follows:

- Three hours in 3-hour barriers

- Ninety minutes in 2-hour

- Forty-five minutes in one-hour barriers

- Twenty minutes in thirty-minute barriers

Labels on fire door assemblies must be maintained in legible condition.  (For full text, refer to NFPA 101-2012: 8.3.4,2; Table8.3.4.2; 8.3.3.2.3; NFPA 80-2010: 5.2.13.3

LS.05.05.10EP5 The space around pipes, conduits, bus duct cables, wire, air ducts, or pneumatic tubes penetrating fire-rated walls or floors are protected with an approved fire-rated material.  For full text, refer to NFPA 101-2012: 8-35

Note: Non-approved polyurethane expanding foam is not accepted fire-rated material for this purpose.

LS.05.01.10EP6- Doors requiring a fire rating of ¾ of an hour or longer are free of coverings, decorations, or other objects applied to the door face, except informational signs, which are applied with adhesive only.  (For full text, refer to NFPA 80-2010; 4.1.4)

LS.05.01.10EP7- The hospital meets all other Life Safety Code requirements, including vertical openings,  related to NFPA 101-2012 38/39.1.

### Recommended Documents:

Policy for Building and Fire Protection Features

Examples:

BF-LS.05.01.10EP1-7 - Building and Fire Protection Features