~Fire Extinguishing Systems

Standard LS.05.01.35

The hospital provides and maintains systems for extinguishing fires.

LS.05.01.35EP1-   For new construction, a process for emergency response notification is provided and includes notifying both of the following:

- Fire department in accordance with NFPA 101-2012; 9.6.4

- Local emergency organization, if provided

- (For full text, refer to NFPA 101-2012: 38.3.4.4)

LS.05.01.35EP2-   For existing construction, notification of emergency forces is accomplished in accordance with NFPA 101-2012;9.6.4 when the existing fire alarm system is replaced. (For full text, refer to NFPA 101-2012: 39.3.4.4)

LS.05.01.35EP3-    The travel distance from any point to the nearest portable fire extinguisher is 75 feet or less.  Portable fire extinguishers have appropriate signage, are installed in a cabinet or secured on a hanger made for the extinguisher, and are at least 4 inches off the floor.  Those fire extinguishers that are 40 pounds or less are installed so the top is not more than 5 feet above the floor.   (For full text, refer to NFPA 101-2012: 38/39.3.5; 9.7.4.1)

LS.05.01.35EP4-   Sprinklers are not damaged.  They are also free from corrosion, foreign materials, and paint and have necessary escutcheon plates installed.

LS.05.01.35EP5-    There are 18 inches or more of space maintained below the sprinkler to the top of the storage.  Note: Perimeter wall and stack shelving may extend up to the ceiling when not located directly below a sprinkler head.

LS.05.01.35EP6-  The hospital meets all other Life Safety Code extinguishing requirements related to NFPA 101-2012:  38/39.3.5

- Recommended Documents:

Policy for determining compliance

Examples:

FS-LS.02.01.35EP1-14 Fire Extinguishing Systems