POLICY

It is the policy of <<Facility Name>> that all ventilation systems shall be installed and maintained in a manner that will ensure that the appropriate pressure relationships, air exchange rates, and filter efficiencies for ventilation systems that serve areas specially designed to control contaminants (e. g., biological agents, gases, fumes)

PROCEDURE

- The organization designs, installs, and maintains ventilation equipment in non–critical care areas to provide appropriate pressure relationships, temperature, and humidity. The non–critical care areas are general care nursing units; clean and soiled utility rooms in acute care areas; laboratories, pharmacies, diagnostic and treatment areas, food preparation areas, and other support departments.

- For all the areas clinical or non-clinical that require pressure relationship, temperature or humidity, the Attachment I can be used to determine the areas and their criteria for design and guidelines.

- All testing, except the construction areas, is scheduled through the appropriate group or project manager.  All documentation pertaining to these tests is maintained in the <<Engineering Department>>.  The project manager maintains the active construction areas documentation until the project is complete.  The associated documentation is then turned over to the <<Engineering Department Director>>.

- Maintaining the appropriate level of temperature and humidity shall be based on a utility system risk assessment and be monitored on a regular basis based on the risks in collaboration with <<Infection Prevention and Control, Engineering, and Surgery>> clinical staff. The temperature and humidity system is monitored through the building automation system and monitoring system. When monitoring system is out of range, an alert will be sent to <<Engineering and/or clinical staff>>.  (Alerts are delayed by 60 minutes to help reduce nuisance alarms.)  Should the system fall out of the appropriate range, plant engineer staff will adjust the appropriate systems to maintain the desired ranges of temperature and humidity in the operating rooms.  Verification that the appropriate ranges for temperature and humidity are being maintained after system adjustments is done through the monitoring systems.

- If the temperature or humidity sustains outside the range set parameters, the <<Engineering>> technician will acknowledge the alarm and monitor the system. This will be logged into their daily log. If the temperature or humidity sustains for more than 4 hours and 4 alarms, the technician will attempt adjustments to the system and check the AHU serving that area. If the temperature or humidity sustains for more than 28 hours after adjustments and evaluating the system, the <<Infection Control Practitioner, the OR clinical director and the Administrator on Call>> will be notified to assess the situation.

- Deficiencies and corrective actions will be reported to the EOC Committee as appropriate.

- A qualified service provider is engaged to verify volume flow rates (air exchange rates, and positive or negative pressure rates) and pressure relationships as part of the commissioning of all new building projects and major space renovations.  In addition, the air volume flow rates and pressure relationships are tested periodically throughout the hospital including investigation of complaints related to indoor air quality.  The results of testing are used to adjust the performance of air handling systems by changing control software parameters and mechanical or electrical controls.

- If system performance cannot be adjusted to meet code requirements or occupant needs, the <<Engineering Department>> works with appropriate Infection Control and clinical staff to develop temporary management practices to mitigate issues.  In addition, a recommendation for upgrading or replacing the equipment involved is prepared and submitted to the CEO and Board as appropriate.

- Biological Safety Cabinets (BSC) and Chemical Fume Hoods (CFH) are tested semi-annually and any filter changed as required.

Attachment:

Attachment I- Form- Air Pressure Relations, Temperature & Humidity in Non-Critical Areas (UT-EC.02.05.01EP16 b)