## Weekly Generator Maintenance Lo
<<Facility Name>>
<<City, State>>
Weekly Generator Maintenance Log
(This form can be used to estimate the output in Amps when the nameplate rating is in Kilowatts)
Generator: <<Identifying name>> |  |  |  |  | Date:
Enter data into red cell to calculate output in Amps and 30% operational level*
Normal Operating Voltage | 208 | Volts
Generator Output in KW (Nameplate rating) | 200 | Kilowatts
Conversion into Watts | 200000 | Watts
Power Factor (PF) ( usually considered .8) | 0.8 | PF
Output in Amps† | 694.7532 | Amps
Assuming 100% efficiency
30 % of nameplate rating in Amps calculate to be: | 208.426 | Amps
Activities (as applicable) | Visual insp. | Check | Change | Test | Clean | Frequency | Check below areas completed
Fuel | [6 empty] | Yes | No | N/A
1. Main Supply Tank Level |  | X |  |  |  | Weekly
2. Day Tank Level | X | X |  |  |  | Weekly
3. Day tank float switch | X | X |  |  |  | Weekly
4. Supply or transfer pump operation | X |  |  | X |  | Weekly
5. Solenoid valve operations | X |  |  | X |  | Weekly
6. Strainer, filter, dirt leg, or combination |  |  |  |  | X | Quarterly
7. Water in system |  | X |  |  | X | Weekly
8. Flexible hose and connectors | X |  | R |  |  | Weekly
9. Tank vents and overflow piping unobstructed |  | X |  | X |  | Annual
10. Piping | X |  |  |  |  | Annual
11. Gasoline in main tank (when used) |  |  | R |  |  | Annual
Lubrication
1. Oil level | X | X |  |  |  | Weekly
2. Oil change |  |  | R |  |  | Annual
3. Oil filter(s) |  |  | R |  |  | Annual
4. Lube oil heater |  | X |  |  |  | Weekly
5. Crankcase breather | X |  | R |  | X | Quarterly
Cooling System
1. Level | X | X |  |  |  | Weekly
2. Antifreeze protection level |  |  |  | X |  | Semi Annual
3. Antifreeze |  |  | R |  |  | Annual
4. Adequate cooling water to heat exchanger |  | X |  |  |  | Weekly
5. Rod out heat exchanger |  |  |  |  | X | Annual
6. Adequate fresh air through radiator |  | X |  |  |  | Weekly
7. Clean exterior of radiator |  |  |  |  | X | Annual
8. Fan and alternator belt | X | X |  |  |  | Monthly
9. Water pump(s) | X |  |  |  |  | Weekly
10. Condition of flexible hoses and connection | X | X |  |  |  | Weekly
11. Jacket water heater |  | X |  |  |  | Weekly
12. Inspect duct work, clean louvers | X | X |  |  | X | Annual
13. Louver mothers and controls | X |  |  | X | X | Annual
Exhaust System
1. Leakage | X | X |  |  |  | Weekly
2. Drain condensate trap |  | X |  |  |  | Weekly
3. Insulation and fire hazards | X |  |  |  |  | Quarterly
4. Excessive back pressure |  |  |  | X |  | Annual
5. Exhaust system hangers and supports | X |  |  |  |  | Annual
6. Flexible exhaust section | X |  |  |  |  | Semi Annual
Electrical System
1. General inspection | X |  |  |  |  | Weekly
2. Tighten control and power wiring connections |  | X |  |  |  | Annual
3. Wire chafing where subject to movement | X | X |  |  |  | Quarterly
4. Operation of safeties and alarms |  |  |  | X |  | Semi Annual
5. Boxes, panels and cabinets |  |  |  |  | X | Semi Annual
6. Circuit breakers and fuses | X | X | R | X | X | Monthly
7. Transfer switch main contracts | X |  |  |  | X | Annual
8. Calibration of voltage-sensing relays/device |  | X |  | X |  | Annual
9. Wire insulation breakdown |  |  |  | X |  | 5yr 500hrs
Prime Mover
1. General inspection | X |  |  |  |  | Weekly
2. Service air cleaner |  |  | R |  | X | Semi Annual
3. Governor oil level and linkage | X | X |  |  |  | Monthly
4. Governor oil |  |  | R |  |  | Annual
5. Ignition system-plugs, points, coil, cap, rotor, secondary wire insulation | X | X | R | X | X | Annual
6. Choke setting and carburetor adjustment |  | X |  |  |  | Semi Annual
7. Injector pump and injectors for flow rate pressure and/or spray pattern |  |  |  | X |  | Annual
8. EPS at minimum of 80% nameplate rating |  |  |  | X |  | 3yr 4hrs
9. Valve clearance |  |  |  | X |  | 3yr 500hrs
10. Torque bolts |  |  |  | X |  | 3yr 500hrs
Generator
1. Brush length, appearance, free to move in holder | X | X |  |  | X | Semi Annual
2. Commutator and slip rings | X |  |  |  | X | Annual
3. Rotor and stator | X |  |  |  | X | Annual
4. Bearings | X |  | R |  |  | Annual
5. Bearing grease |  | X | R |  |  | Annual
6. Exciter | X | X |  |  | X | Annual
7. Voltage regulator | X | X |  |  | X | Annual
8. Measure and record* resistance readings of windings with insulation tester (Megger) |  |  |  | X |  | Annual
9. General condition EPSS any unusual condition of vibration, leakage, noise, temperature, or deterioration | X |  |  |  | X | Weekly
10. Service room or housing housekeeping | X |  |  |  | X | Weekly
11. Restore system to automatic operation condition | X |  |  |  |  | Weekly
*Recording ________
Notes:
Report any unusual conditions ASAP | Key: | X-Action | R-replace when needed
Technician Signature |  |  |  | Date
† Amps = KW / (Voltage x PF x 1.73)