# POLICY

<<Facility Name>>performs all appropriate tests on each automatic and manual transfer switch connected to the emergency generators.

# PROCEDURE

- Each automatic transfer switch (ATS) and manual transfer switch are tested at least monthly.

- If load banks are routinely used as part of the load during testing to raise the load above 30% of capacity, there must be a method to automatically transfer to the actual load in the case of a failure of the primary sources of power.

- All automatic transfer switches shall be electrically operated from the standard to the alternate position, and return to the standard position.

- The time of the delay for transfer shall not exceed 10 seconds.

- If appropriate, a different ATS should be used to initiate the emergency generator monthly test.

- The completion date and the results of the tests are documented. And will be maintained by the <<Engineering Department>>.

ATTACHMENT:

Attachment I- Form-Automatic and Manual Transfer Switch Testing (UT-EC.02.05.07EP7 b)