# This trans-filling policy is only necessary for those facilities that transfil gases

# POLICY

It is the policy of <<Facility Name>> to ensure that trans-filling is conducted in a safe manner and that is consistent with a combination of applicable regulations and best practices.

PROCEDURE

- Trans-filling is not conducted in any patient care room or any compartment where patient care is conducted.

- A designated area is used away from any section of the hospital where patients are housed, treated, or examined. The designated area is located in <<name location>>.

- The designated area is separated by a barrier of at least 1-hour fire-resistant construction from any patient care areas.

- Only the same gas trans-filling (no mixing of different compressed gases) is conducted.

- Transfilling of liquid oxygen is only done in an area that is mechanically ventilated, sprinklered, and has ceramic or concrete flooring.

- Storage and use of liquid oxygen in base reservoir containers and portable containers comply with sections NFPA 99-2012: 11.7.2-11.7.4.